## Introduction
Logix 5000 Controller and I/O Fault Codes
About This Publication | This publication lists the fault codes for Logix 5000 Controllers.
For more information see:
| ControlLogix 5580 and GuardLogix 5580 Controllers User Manual | 1756-UM543
| CompactLogix 5380 and Compact GuardLogix 5380 Controllers User Manual | 5069-UM001
| CompactLogix 5480 Controllers User Manual | 5069-UM002
Important: Rockwell Automation is not responsible for any content or format changes made by other parties after downloading this spreadsheet file. The original file can be re-downloaded at any time.
TIP: When you search for information in a spreadsheet, set the search options to search the workbook, rather than the current sheet (tab).
Allen-Bradley, Compact I/O, CompactLogix, ControlBus, DriveGuard, GuardLogix, GuardMotion, DH+, FLEX, Logix 5000, PLC-5, POINTBus, POINT I/O, Rockwell Automation, RSLinx, RSLogix 5000, RsNetWorx, and Studio 5000 Logix Designer are trademarks of Rockwell Automation, Inc. CIP, CIP Motion, CIP Sync, ControlNet, and EtherNet/IP are trademarks of ODVA, Inc. Trademarks not belonging to Rockwell Automation are property of their respective companies.

## Summary of Changes
Summary of Changes
Date | Changes
August 2021 | First release as an Excel spreadsheet

## Logix5000 controller
Logix 5000™ Controller and I/O Fault Codes
For more information see:
http://literature.rockwellautomation.com/idc/groups/literature/documents/pm/1756-pm014_-en-p.pdf
Fault Type | Fault Code | Studio 5000 Logix Designer® Application Display Text | Fault | Corrective Action | Major/Minor | Fault Type Name
1 | 1 | Major Fault T01:C01 - Power-up Fault: Power lost and restored in RUN mode. | The controller powered on in Run mode. | Execute the power up handler. | Major | Power Up
1 | 2 | Minor Fault T01:C02 - Power-up Fault: AC power loss detected. Chassis active until DC power cannot be maintained. | AC power loss detected. Chassis active until DC power cannot be maintained. | Legacy. Now an unused fault code. | Minor | Power Up
1 | 15 | Minor Fault T01:C15 - Power-up Fault: I/O Power fault detected. | A 1769 power supply is connected directly to the controller’s 1768 CompactBus, with an invalid configuration. The 1768 power supply powering the controller has failed. | Remove the power supply from the 1768 CompactBus and cycle power to the system. Replace the power supply. | Minor | Power Up
1 | 16 | Major Fault T01:C16 - Power-up Fault: I/O Communications Configuration fault detected. | I/O communication configuration fault detected. (CompactLogix™ 1768-L4x controllers only.) | Reconfigure the number of communication modules on the 1768 bus side of the controller: - 1768-L43 has a maximum of two modules. - 1768-L45 has a maximum of four modules. - Up to four Sercos modules - Up to two NetLinx communication modules | Major | Power-up
1 | 29 | Minor Fault T01:C29 - Power-up Fault: Voltage has exceeded operating limits. | Voltage has exceeded operating limits. | Legacy. Now an unused fault code. | Minor | Power Up
1 | 40 | Major Fault T01:C40 - Power-up Fault: Energy Storage Module/Battery failed during power down. | If the controller uses a battery, the battery does not contain enough charge to save the user program on power-down. If the controller uses an ESM (Energy Storage Module), the ESM does not contain enough charge to save the user program on power-down. | For controllers that use a battery, replace the battery. For controllers that use an ESM (Energy Storage Module): - Allow the ESM to fully charge before powering down the controller. - Replace the ESM if the ESM is removable, or replace the controller if the ESM is not removable. If the problem persists, contact Rockwell Automation support. | Major | Power Up
1 | 60 | Major Fault T01:C60 - Power-up Fault: Non-recoverable Fault. | For a controller with no memory card installed, the controller: - Detected a non-recoverable fault. - Cleared the project from memory. | 1. Clear the fault. 2. Download the project. 3. Change to Remote Run or Run mode. Follow these steps if the fault persists. 1. Before you cycle power to the controller, record the state of the OK and RS232 status indicators. 2. Contact Rockwell Automation support. | Major | Power Up
1 | 61 | Major Fault T01:C61 - Power-up Fault: Non-recoverable Fault with saved Diagnostic Information. | For a controller with a memory card installed, the controller: - Detected a non-recoverable fault. - Wrote diagnostic information to the memory card. - Cleared the project from memory. | 1. Clear the fault. 2. Download the project. 3. Change to Remote Run or Run mode. If the fault persists, contact Rockwell Automation support. | Major | Power Up
1 | 62 | Major Fault T01:C62 - Power-up Fault: Non-recoverable Fault with saved diagnostic information and stored user program. | For a controller with a Secure Digital (SD) card installed, the controller: - Detected a nonrecoverable fault. - Wrote diagnostic information to the memory card. When in this state, the controller does not open any connections or allow a transition to Run mode. | 1. Clear the fault. 2. Download the project. 3. Change to Remote Run or Run mode. If the fault persists, contact Rockwell Automation support. | Major | Power Up
3 | 0 | Minor Fault T3:C0 - I/O Fault: Compact I/O end cap missing. | Compact I/O™ end cap missing. | Install the end cap. | Minor | I/O
3 | 1 | Minor Fault T03:C01 - I/O Fault: PointBus backplane bus off. | PointBus™ backplane bus off condition. The connections between the controller and the I/O modules are broken. | Complete these steps to identify the source of the BUS OFF fault: 1. The number of local expansion modules in the project matches the number of modules that are physically installed in the system. 2. All mounting bases are locked and I/O modules are securely installed on mounting bases. 3. All 1734 POINT I/O™ modules are configured to use the Autobaud rate. If these steps do not remedy the fault condition, contact Rockwell Automation support. | Minor | I/O
3 | 16 | Major Fault T03:C16 - I/O Fault: I/O module connection failed on required module. | A required I/O module connection failed. | Check the: - I/O module is in the chassis. - Electronic keying requirements. - Controller Properties Major Fault tab and the Module Properties Connection tab for more information about the fault. | Major | I/O
3 | 20 | Major Fault T03:C20 - I/O Fault: Unable to read ControlBus™ chassis information. Chassis may be bad. | Possible fault with the chassis. | Not recoverable. Replace the chassis. | Major | I/O
3 | 21 | Major Fault T03:C21 - I/O Fault: Unable to read ControlBus chassis information. Chassis may be bad. | Possible fault with the chassis. | Not recoverable. Replace the chassis. | Major | I/O
3 | 23 | Major Fault T03:C23 - I/O Fault: At least one required connection not established before going into RUN mode. | At least one required connection was not established before going to Run mode. | Wait for the controller I/O light to turn green before changing to Run mode. | Major | I/O
3 | 94 | Minor Fault T03:C94 - I/O Fault: Module RPI overlap detected. | Module RPI overlap detected. The current RPI update of an I/O module overlaps with its previous RPI update. | Set the RPI rate of the I/O modules to a higher numerical value. Rockwell Automation recommends that the CompactLogix 5370 L2 and CompactLogix 5370 L3 control systems do not run with Module RPI Overlap faults. | Minor | I/O
3 | 100 | Minor Fault T03:C100 - I/O Fault: I/O module does not support data integrity. | I/O module does not support data integrity. | Legacy. Now an unused fault code. | Minor | I/O
4 | 4 | Minor Fault T04:C04 - Program Fault: Arithmetic overflow. Result of an arithmetic instruction out of range. | The resul of an arithmetic operation is out of range. | Examine the arithmetic operations (order) or adjust the values. | Minor | Program
4 | 5 | Minor Fault T04:C05 - Program Fault: GSV/SSV object address invalid. | In a GSV/SSV instruction, the specified instance was not found. | Check the instance name. | Minor | Program
4 | 6 | Minor Fault T04:C06 - Program Fault: GSV/SSV operand invalid. | In a GSV/SSV instruction, either the: - Specified Class name is not supported. - Specified Attribute name is not valid. | Check the Class name and Attribute name. | Minor | Program
4 | 7 | Minor Fault T04:C07 - Program Fault: GSV/SSV destination tag too small to hold all data. | The GSV/SSV destination tag was too small to hold the data. | Fix the destination so it has enough space. | Minor | Program
4 | 16 | Major Fault T04:C16 - Program Fault: Unknown instruction encountered. | Unknown instruction encountered. | Remove the unknown instruction. This probably happened due to a program conversion process. | Major | Program
4 | 20 | Major Fault T04:C20 - Program Fault: Array subscript too large, or CONTROL data type POS or LEN invalid. | Array subscript too large, or CONTROL data type .POS or .LEN value is invalid. | Adjust the value to be within the valid range. Do not exceed the array size or go beyond dimensions defined. | Major | Program
4 | 21 | Major Fault T04:C21 - Program Fault: CONTROL data type LEN or POS less than 0. | Control structure .LEN or .POS < 0. | Adjust the value so it is > 0. | Major | Program
4 | 24 | Major Fault T04:C24 - Program Fault: Unknown data type passed to subroutine. | Unknown data type passed to subroutine. | Legacy. Now an unused fault code. | Major | Program
4 | 30 | Minor Fault T04:C30 - Program Fault: ASCII instruction failed. | An ASCII instruction failed.. Bad parameters passed through to the ASCII port. | Verify the ASCII configuration settings. | Minor | Program
4 | 31 | Major Fault T04:C31 - Program Fault: JSR or RET did not pass as many parameters as expected. | The parameters of the JSR instruction do not match those of the associated SBR or RET instruction. | Pass the appropriate number of parameters. If you pass too many parameters, the extra ones are ignored without any error. | Major | Program
4 | 32 | Minor Fault T04:C32 - Program Fault: Routine type not supported. | Routine type not supported. | Legacy. Now an unused fault code. | Minor | Program
4 | 34 | Major Fault T04:C34 - Program Fault: A timer instruction had a negative value for its PRE or ACC. | A timer instruction has a negative preset or accumulated value. | Fix the program so that it cannot load a negative value into timer preset or accumulated value. | Major | Program
4 | 35 | PID delta time was less than 0. | PID delta time less than zero. | Adjust the PID delta time so that it is > 0. | Minor | Program
4 | 36 | PID setpoint out of range for target module. | PID setpoint out of range. | Adjust the setpoint so that it is within range. | Minor | Program
4 | 42 | Major Fault T04:C42 - Program Fault: JMP to a label that did not exist or was deleted. | JMP to a label that did not exist or was deleted. | Correct the JMP target or add the missing label. | Major | Program
4 | 51 | Minor Fault T04:C51 - Program Fault: LEN value outside DATA limit. | The .LEN value of the string tag is greater than the DATA size of the string tag. | 1. Check that no instruction is writing to the LEN member of the string tag. 2. In the LEN value, enter the number of characters that the string contains. | Minor | Program
4 | 52 | Minor Fault T04:C52 - Program Fault: Defined string size is invalid. | The output string is larger than the destination. | Create a new string data type that is large enough for the output string. Use the new string data type as the data type for the destination. | Minor | Program
4 | 53 | Minor Fault T04:C53 - Program Fault: Numeric result cannot fit in destination. | The output number is beyond the limits of the destination data type. | Either: - Reduce the size of the ASCII value. - Use a larger data type for the destination. | Minor | Program
4 | 54 | Minor Fault T04:C54 - Program Fault: BufferSize value reduced amount of data. | BufferSize value reduced amount of data. | Legacy. Now an unused fault code. | Minor | Program
4 | 55 | Minor Fault T04:C55 - Program Fault: SerialPort Control Len value was incorrect. | SerialPort Control .LEN value was incorrect. | Legacy. Now an unused fault code. | Minor | Program
4 | 56 | Minor Fault T04:C56 - Program Fault: Invalid Start and/or Quantity value. | The Start or Quantity value is invalid. | Check the following: - The Start value is between 1 and the DATA size of the Source. - The Start value plus the Quantity Value is less than or equal to the DATA size of the Source. | Minor | Program
4 | 57 | Minor Fault T04:C57 - Program Fault: Cannot execute AHL when SerialPort set to NoHandshaking. | The AHL instruction failed to execute because the serial port is set to no handshaking. | Either: - Change the Control Line setting of the serial port. - Delete the AHL instruction. | Minor | Program
4 | 82 | Major Fault T04:C82 - Program Fault: Could not re-enter an executing SFC routine. | A sequential function chart (SFC) called a subroutine and the subroutine tried to jump back to the calling SFC. This occurs when the SFC uses either a JSR or FOR instruction to call the subroutine. | Remove the jump back to the calling SFC. | Major | Program
4 | 83 | Major Fault T04:C83 - Program Fault: Value out of range. | The data tested was not inside the required limits. This occurs with array subscripts used with Boolean arrays and bit level addressing. | Adjust the value to be within the valid range. Do not exceed the array size or go beyond the dimensions defined. | Major | Program
4 | 84 | Major Fault T04:C84 - Program Fault: Stack overflow. Stack too small to perform operation. | Stack overflow. | Reduce the subroutine nesting levels or the number of parameters passed. | Major | Program
4 | 85 | Major Fault T04:C85 - Program Fault: Invalid routine type. | Invalid routine type. | Use a valid routine type. | Major | Program
4 | 86 | Minor Fault T04:C86 - Program Fault: Access violation in user program. | Access violation in user program. | Contact Rockwell Automation Technical Support. | Minor | Program
4 | 87 | Minor Fault T04:C87 - Program Fault: External routine DLL load failed. Perhaps a DLL on which it depends is missing. | External routine DLL load failed. | DLL missing or malformed. Confirm and adjust. | Minor | Program
4 | 88 | Minor Fault T04:C88 - Program Fault: Exception in external routine DLL. | Exception in external routine DLL. | Troubleshoot the external routine DLL. | Minor | Program
4 | 89 | Major Fault T04:C89 - Program Fault: Target step does not exist in specified routine. | In an SFR instruction, the target routine does not contain the target step. | Correct the SFR target or add the missing step. | Major | Program
4 | 90 | Major Fault T04:C90 - Program Fault: A safety instruction occurs outside a safety task. | A safety instruction occured outside a safety task. | Only use the instruction in a safety task. | Major | Program
4 | 91 | Major Fault T04:C91 - Program Fault: Equipment phase instruction cannot be called from a program. | Equipment Phase instruction is being called from outside an Equipment Phase program. | Only use the instruction in an Equipment Phase program. | Major | Program
4 | 94 | Major Fault T04:C94 - Program Fault: Nesting limits exceeded. | Nesting limits exceeded. | Restructure the project to reduce the subroutine nesting levels. | Major | Program
4 | 990 | Major Fault T04:C990 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
4 | 991 | Major Fault T04:C991 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
4 | 992 | Major Fault T04:C992 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
4 | 993 | Major Fault T04:C993 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
4 | 994 | Major Fault T04:C994 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
4 | 995 | Major Fault T04:C995 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
4 | 996 | Major Fault T04:C996 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
4 | 997 | Major Fault T04:C997 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
4 | 998 | Major Fault T04:C998 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
4 | 999 | Major Fault T04:C999 - Program Fault: User-defined fault. | User-defined major fault. | User-defined action. | Major | Program
6 | 1 | Major Fault T06:C01 - Watchdog Fault: Task watchdog expired. May have been caused by an infinite loop, a complex program, or a higher priority task. | User task has not completed in the specified period. A program error caused an infinite loop, or the program is too complex to run as quickly as specified, or a higher priority task is keeping this task from finishing. | Take one or more of these steps: - Increase the task watchdog. - Shorten the execution time. - Make the priority of this task higher. - Simplify higher priority tasks. - Move some code to another controller. | Major | Watchdog
6 | 2 | Minor Fault T06:C02 - Watchdog Fault: Periodic task overlap. Task scheduled again before it finished executing. | Periodic task overlap. The task was scheduled again before it finished executing. | Make changes, such as simplifying programs, lengthening the period, or raising the relative priority. | Minor | Watchdog
6 | 3 | Minor Fault T06:C03 - Watchdog Fault: Event task overlap. Task triggered again before it finished executing. | Event task overlap. The task triggered again before it finished executing. | Make changes such as simplifying programs, lengthening the period, raising the relative priority, or slowing the triggering event. | Minor | Watchdog
7 | 40 | Major Fault T07:C40 - Nonvolatile Fault: Store to nonvolatile memory failed. | Store to nonvolatile memory failed. | 1. Try again to store the project to nonvolatile memory. 2. If the project fails to store to nonvolatile memory, replace the memory card. If you are using a 1756-L7x controller, verify that the SD card is unlocked. | Major | Flash Save
7 | 41 | Major Fault T07:C41 - Nonvolatile Fault: Load from nonvolatile memory failed due to controller type mismatch. | Load from nonvolatile memory failed due to controller type mismatch. | Change to a controller of the correct type or download the project and store it on the memory card. | Major | Flash Save
7 | 42 | Major Fault T07:C42 - Nonvolatile Fault: Load from nonvolatile memory failed due to controller revision mismatch. | Load from nonvolatile memory failed because the firmware revision of the project in nonvolatile memory does not match the firmware revision of the controller. | Update the controller firmware to the same revision level as the project that is in nonvolatile memory. | Major | Flash Save
7 | 43 | Major Fault T07:C43 - Nonvolatile Fault: Load from nonvolatile memory failed due to bad checksum. | Load from nonvolatile memory failed due to bad checksum. | Contact Rockwell Automation support. | Major | Flash Save
7 | 44 | Major Fault T07:C44 - Nonvolatile Fault: Failed to restore processor memory. | Failed to restore controller memory. | Contact Rockwell Automation support. | Major | Flash Save
7 | 49 | Minor Fault T07:C49 - Nonvolatile Fault: Controller was loaded from nonvolatile memory. | When the controller loads a project from nonvolatile memory, it logs this minor fault and sets the FaultLog object, MinorFaultBits attribute, bit 7. | Clear the fault. | Minor | Flash Save
7 | 50 | Major Fault T07:C50 - Nonvolatile Fault: Security certificate invalid. | The log file certificate cannot be verified. When the controller starts up it attempts to verify the log file key/certificate combination. Depending on the verification, the controller takes one of the following actions: - If the controller verifies the existing log file certificate, the controller continues with existing log directory. - If the existing certificate cannot be verified, the controller logs a major fault and attempts to create a new certificate. - If the controller successfully creates a new certificate, it creates a backup log subdirectory, moves the existing files to that directory, and continues logging and signing with the new verification key and log file certificate. - If the controller cannot create a new certificate, the controller writes log entries to the existing log directory, but does not update signature files in that directory. | Clear the fault and power cycle the controller. If the problem persists, contact Rockwell Automation support. | Major | Flash Save
8 | 1 | Major Fault T8:C1 - Mode Change Fault: Mode Change inhibited due to download in progress. | Attempted to place controller in Run mode with keyswitch during download. | Wait for the download to complete and clear the fault. | Major | Mode Change
9 | 0 | Minor Fault T09:C00 - Serial Port Fault: Unknown error while servicing serial port. | Unknown error while servicing the serial port. | Contact Rockwell Automation Technical Support. | Minor | Serial Port
9 | 1 | Minor Fault T09:C01 - Serial Port Fault: Problem with hardware control lines. | The CTS line is not correct for the current configuration. | Disconnect and reconnect the serial port cable to the controller. Make sure the cable is wired correctly. | Minor | Serial Port
9 | 2 | Minor Fault T09:C02 - Serial Port Fault: Contents of poll list tag incorrect. | Poll list error. A fault was detected with the DF1 master’s poll list, such as specifying more stations than the size of the file, specifying more than 255 stations, trying to index past the end of the list, or polling the broadcast address (STN #255). | Check for the following errors in the poll list. - Total number of stations is greater than the space in the poll list tag. - Total number of stations is greater than 255. - Current station pointer is greater than the end of the poll list tag. - A station number greater than 254 was encountered. | Minor | Serial Port
9 | 3 | Minor Fault T09:C03 - Serial Port Fault: Master protocol missing Active Station File. | The RS232 DFI Master Active Station tag is unspecified. | Specify a tag to be used for the Active Station Tag in the System Protocol tab of the Controller Properties. | Minor | Serial Port
9 | 5 | Minor Fault T09:C05 - Serial Port Fault: DF1 slave poll timeout. | DF1 slave poll timeout. The poll watchdog has timed out for slave. The master has not polled this controller in the specified amount of time. | Determine and correct delay for polling. | Minor | Serial Port
9 | 9 | Minor Fault T09:C09 - Serial Port Fault: Modem contact lost. | Modem contact lost. DCD or DSR control lines are not being received in proper sequence or state. | Correct modem connection to the controller. | Minor | Serial Port
9 | 10 | Minor Fault T09:C10 - Serial Port Fault: Serial Port is unable to keep up with incomming data. | Data has been dropped or lost from the serial port. | Slow down the rate at which the initiator is sending data. | Minor | Serial Port
9 | 11 | Minor Fault T09:C11 - Serial Port Fault: ACL instruction channel operand is not a valid port. | A channel operand in an ACL instruction channel is not a valid port. | Correct the channel specified in the ACL instruction. | Minor | Serial Port
10 | 10 | Minor Fault T10:C10 - Battery Fault: Battery missing or needs to be replaced. | The battery is missing or needs to be replaced. | Install a new battery. | Minor | Battery
10 | 11 | Minor Fault T10:C11 - Battery Fault: Safety partner battery missing or needs to be replaced. | The battery for the safety partner is missing or needs to be replaced. | Install a new battery. | Minor | Battery
10 | 12 | Minor Fault T10:C12 - Energy Storage Fault: Energy Storage Module not present. | The energy storage module is not installed. If the controller is powered-down, the WallClockTime attribute and program are not maintained. | Install an ESM in the controller. | Minor | Battery
10 | 13 | Minor Fault T10:C13 - Energy Storage Fault: Energy Storage Module incompatible with controller type. | The installed energy storage module is not compatible with the controller. | Replace the installed ESM with one that is compatible with the controller. | Minor | Battery
10 | 14 | Minor Fault T10:C14 - Energy Storage Fault: Energy Storage Module hardware failure. | The energy storage module needs to be replaced due to a hardware fault. It is not capable of maintaining the WallClockTime attribute or controller program at power down. | Replace the ESM. | Minor | Battery
10 | 15 | Minor Fault T10:C15 - Energy Storage Fault: Energy Storage Module energy low. | The energy storage module cannot store enough energy to maintain the WallClockTime attribute or the controller program at power-down. | Replace the ESM. | Minor | Battery
10 | 16 | Minor Fault T10:C16 - UPS Fault: UPS missing or not ready. | The uninterruptible power supply is missing or not ready. | Either: - Install the UPS. - Check the UPS to make sure it is adequately charged to provide backup power in the event of power loss. | Minor | Battery
10 | 17 | Minor Fault T10:C17 - UPS Fault: UPS battery failure. | The uninterruptible power supply battery has failed and needs to be replaced. | Replace the battery in the UPS. | Minor | Battery
11 | 1 | Major Fault T11:C01 - Motion Fault: Actual position of axis exceeded positive overtravel limit. | Actual position of the axis has exceeded positive overtravel limit. | Move axis in negative direction until position is within overtravel limit and then execute Motion Axis Fault Reset. | Major | Motion
11 | 2 | Major Fault T11:C02 - Motion Fault: Actual position of axis exceeded negative overtravel limit. | Actual position of the axis has exceeded negative overtravel limit. | Move axis in positive direction until position is within overtravel limit and then run Motion Axis Fault Reset. | Major | Motion
11 | 3 | Major Fault T11:C03 - Motion Fault: Actual position exceeded position error tolerance. | Actual position the axis has exceeded position error tolerance. | Move the position within tolerance, then run Motion Axis Fault Reset. | Major | Motion
11 | 4 | Major Fault T11:C04 - Motion Fault: Encode channel A, B, or Z connection failed. | Encoder channel A, B, or Z connection is broken. | Reconnect the encoder channel, then run Motion Axis Fault Reset. | Major | Motion
11 | 5 | Major Fault T11:C05 - Motion Fault: Encoder noise event detected, or encoder signals not in quadrature. | Encoder noise event detected or the encoder signals are not in the quadrature. | Fix encoder cabling, then run Motion Axis Fault Reset. | Major | Motion
11 | 6 | Major Fault T11:C06 - Motion Fault: Drive fault. | Drive fault detected. | Clear Drive Fault then run Motion Axis Fault Reset. | Major | Motion
11 | 7 | Major Fault T11:C07 - Motion Fault: Synchronous connection to servo module failed. | Synchronous connection to the servo module failed. | Try these steps: 1. First, run Motion Axis Fault Reset. 2. If that does not work, pull the servo module out and plug it back in. 3. If this does not work, replace the servo module. | Major | Motion
11 | 8 | Major Fault T11:C08 - Motion Fault: Hardware failure in servo module. | Hardware failure detected in the servo module. | Replace the module. | Major | Motion
11 | 9 | Major Fault T11:C09 - Motion Fault: Asynchronous connection to servo module failed. | Asynchronous connection to the servo module failed. | Try these steps: 1. First, run Motion Axis Fault Reset. 2. If that does not work, pull the servo module out and plug it back in. 3. If this does not work, replace the servo module. | Major | Motion
11 | 10 | Major Fault T11:C10 - Motion Fault: Motor fault detected. | Motor fault detected. | See the DriveFaults axis tag for more information. | Major | Motion
11 | 11 | Major Fault T11:C11 - Motion Fault: Motor thermal fault detected. | Motor thermal fault detected. | See the DriveFaults axis tag for more information. | Major | Motion
11 | 12 | Major Fault T11:C12 - Motion Fault: Drive thermal fault detected. | Drive thermal fault detected. | See the DriveFaults axis tag for more information. | Major | Motion
11 | 13 | Major Fault T11:C13 - Motion Fault: SERCOS comm fault detected. | SERCOS communication fault detected. | Verify the integrity of the SERCOS fiber-optic ring network and the devices on it. | Major | Motion
11 | 14 | Major Fault T11:C14 - Motion Fault: Drive Enable Input 1) was inactive prior during an attempt to enable the drive, or 2) transitioned to inactive while the drive was enabled. | Drive enable input was inactive during an attempt to enable the drive or transitioned to inactive while the drive was enabled. | Re-enable the drive enable input and clear the fault. | Major | Motion
11 | 15 | Major Fault T11:C15 - Motion Fault: Drive Phase Loss fault detected. | Drive phase loss fault detected. | Restore full power connection to the drive and clear the fault. | Major | Motion
11 | 16 | Major Fault T11:C16 - Motion Fault: A Guard Fault has been detected by the drive. | DriveGuard® fault detected. | See the GuardFaults axis tag for more information. | Major | Motion
11 | 32 | Major Fault T11:C32 - Motion Fault: Motion Task overlap. Coarse update rate too high. | The motion task experienced an overlap. The coarse update rate is too high. | The group’s course update rate is too high to maintain correct operation. Clear the group fault tag, raise the group’s update rate, and then clear the major fault. | Major | Motion
11 | 33 | Major Fault T11:C33 - Motion Fault: Coordinated System Time reference has been lost. | Coordinated System Time reference has been lost. | Check the condition of the CST master in the backplane. | Major | Motion
12 | 32 | Major Fault T12:C32 - Safety Fault: Disqualified secondary became primary. | A disqualified secondary controller cycled power and no partner chassis or controller was found upon powerup. | Verify the following items. - A partner chassis is connected. - Power is applied to both redundant chassis. - Partner controllers have the same catalog number, slot number, and firmware revision. | Major | Redundancy
12 | 33 | Major Fault T12:C33 - Safety Fault: No partner found after switchover. | An unpartnered controller has been identified in the new primary chassis after a switchover. | Either: - Remove the unpartnered controller and troubleshoot the cause of the switch over. - Add a partner controller to the secondary chassis, troubleshoot the cause of the switch over, and synchronize the system. | Major | Redundancy
12 | 34 | Major Fault T12:C34 - Safety Fault: Keyswitch Positions of Primary and Secondary Controllers Mismatched | Just after a switchover occurs, the keyswitch positions of the primary and secondary controllers are mismatched. The old primary controller is in Program mode and the new primary controller is in Run mode. | Either: - Change the keyswitches from Run to Program to Run mode twice to clear the fault. - Use the Logix Designer application to go online with the controllers. Then, clear the faults and change both the controller's mode to Run. | Major | Redundancy
13 | 21 | Minor Fault T13:C21 - Real Time Clock Fault: Wall Clock Time out of range. | The wall clock time is out of range. | Verify the Wall Clock Time is set to the correct date/time. | Minor | Real Time Clock
14 | 1 | Major Fault T14:C01 - Safety Task Fault: Task watchdog expired. May have been caused by infinite loop, complex program, higher priority task, or removal of Safety partner. | Safety Task watchdog expired. Safety task has not completed in a specified period. A program error caused an infinite loop, the program is too complex to run as quickly as specified, a higher priority task is keeping this task from finishing, or the safety partner has been removed. | Clear the fault. If a safety task signature exists, safety memory is re-initialized and the safety task begins executing. If a safety task signature does not exist, you must re-download the program to allow the safety task to run. Reinsert the safety partner, if it was removed. | Major | Safety
14 | 2 | Major Fault T14:C02 - Safety Task Fault: An error exists in a routine of the Safety task. | An error exists in a routine of the safety task. | Correct the error in the user-program logic. | Major | Safety
14 | 3 | Major Fault T14:C03 - Safety Task Fault: Safety partner is missing. | Safety partner is missing. | Install a compatible safety partner. | Major | Safety
14 | 4 | Major Fault T14:C04 - Safety Task Fault: Safety partner is unavailable. | Safety partner is unavailable. | Install a compatible safety partner. | Major | Safety
14 | 5 | Major Fault T14:C05 - Safety Task Fault: Safety partner hardware is incompatible. | Safety partner hardware is incompatible. | Install a compatible safety partner. | Major | Safety
14 | 6 | Major Fault T14:C06 - Safety Task Fault: Safety partner firmware is incompatible. | Safety partner firmware is incompatible. | Update the safety partner so that the firmware major and minor revision matches the primary controller. | Major | Safety
14 | 7 | Major Fault T14:C07 - Safety Task Fault: Safety task is inoperable. | The safety logic is invalid. For example, a mismatch in Logix exists between the primary controller and safety partner, a watchdog timeout occurred, or memory is corrupt. | Clear the fault. If a safety task signature exists, safety memory is re-initialized via the safety task signature and the safety task begins executing. If a safety task signature does not exist, you must download the program again to allow the safety task to run. | Major | Safety
14 | 8 | Major Fault T14:C08 - Safety Task Fault: Safety partner's time is not synchronized with primary. | Coordinated system time (CST) not found. The safety partner's time is not synchronized with primary. | Clear the fault. Configure a device to be the CST master. | Major | Safety
14 | 9 | Major Fault T14:C09 - Safety Task Fault: A non-recoverable fault has occurred in Safety Partner. | A nonrecoverable fault occurred in the safety partner. | Clear the fault and download the program. If the fault persists, replace the safety partner. | Major | Safety
14 | 12 | Minor Fault T14:C12 - Safety Fault: Safety partner detected when the project safety level is SIL2/PLd. | The safety partner detected when the project safety level is SIL2/PLd. | If your desired safety level is SIL2/PLd, remove the safety partner (since it does not participate in a SIL2/PLd configuration). If your desired safety level is SIL3/PLe, change the project safety level to SIL3/PLe. | Minor | Safety
17 | 0 | Minor Fault T17:C00 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 1 | Minor Fault T17:C01 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 2 | Minor Fault T17:C02 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 3 | Minor Fault T17:C03 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 4 | Minor Fault T17:C04 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 5 | Minor Fault T17:C05 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 6 | Minor Fault T17:C06 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 7 | Minor Fault T17:C07 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 8 | Minor Fault T17:C08 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 9 | Minor Fault T17:C09 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 10 | Minor Fault T17:C10 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 11 | Minor Fault T17:C11 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 12 | Minor Fault T17:C12 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 13 | Minor Fault T17:C13 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 14 | Minor Fault T17:C14 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 15 | Minor Fault T17:C15 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 16 | Minor Fault T17:C16 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 17 | Minor Fault T17:C17 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 18 | Minor Fault T17:C18 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 19 | Minor Fault T17:C19 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 20 | Minor Fault T17:C20 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 21 | Minor Fault T17:C21 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 22 | Minor Fault T17:C22 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 23 | Minor Fault T17:C23 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 24 | Minor Fault T17:C24 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 25 | Minor Fault T17:C25 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 26 | Minor Fault T17:C26 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 27 | Minor Fault T17:C27 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 28 | Minor Fault T17:C28 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 29 | Minor Fault T17:C29 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 30 | Minor Fault T17:C30 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 31 | Minor Fault T17:C31 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 32 | Minor Fault T17:C31 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 33 | Minor Fault T17:C33 - Diagnostic Fault: A runtime diagnostic failed to complete, please contact technical support with the fault type and fault code. | An internal controller diagnostic failed. Upload and save program before controller is powered down. | Contact Rockwell Automation Technical Support with the fault type and fault code logged. | Minor | Diagnostic
17 | 34 | Major Fault T17:C34 - Diagnostic Fault: Controller internal temperature has exceeded operating limit. | Controller internal temperature has exceeded the operating limit. | Measures should be taken to reduce the ambient temperature of the module. Follow the recommended limits for the ambient (inlet) temperature and apply the required clearance around the chassis. | Major | Diagnostic
17 | 35 | Minor Fault T17:C35 - Diagnostic Fault: Controller internal temperature is approaching operating limit. | Controller internal temperature is approaching the operating limit. | Measures should be taken to reduce the ambient temperature of the module. Follow the recommended limits for the ambient (inlet) temperature and apply the required clearance around the chassis. | Minor | Diagnostic
17 | 36 | Minor Fault T17:C36 - Diagnostic Fault: A fan has been removed, or is not maintaining desired speed. | A fan has been removed, or is not maintaining the desired speed. | Applies to CompactLogix 5480 Controllers. Check the device fans for connection or maintenance issues. | Minor | Diagnostic
17 | 37 | Major Fault T17:C37 - Diagnostic Fault: Controller has recovered from an internal temperature fault. | Controller has recovered from an internal temperature fault. | Generated when the controller recovers from automatic shutdown. Shutdown occurs when the module temperature exceeds the temperature threshold of the preservation fault. When the temperature decreases to a suitable level, this re-enables the controller voltages and generates the Type 17, Code 37 fault. | Major | Runtime Diagnostic
18 | 1 | Major Fault T18:C01 - CIP Motion Fault: A standard Initialization Fault has been detected by the drive. | The CIP Motion™ drive did not initialized correctly. | To determine corrective action, see the Initialization Fault attributes. The corresponding bit indicates the cause of the fault. 1: Boot Block Checksum Fault 2: Main Block Checksum Fault 3: Nonvolatile Memory Checksum Fault | Major | CIP Motion
18 | 2 | Major Fault T18:C02 - CIP Motion Fault: A manufacturer specific Initialization Fault has been detected by the drive. | The CIP Motion drive did not initialized correctly. This fault indicates a manufacturer-specific initialization fault. | To determine corrective action, see the Initialization Fault Mfg attributes. The corresponding bit indicates the cause of the fault. 1: Feedback Data Corruption 2: Feedback Data Range 3: Feedback Communication Startup 4: Feedback Absolute Overspeed 5: Feedback Absolute Power Off Travel 6: Feedback Absolute Startup Speed 7: Commutation Offset Uninitialized 12: Invalid FPGA Image 14: Invalid Safety Firmware 15: Power Board 16: Illegal Option Card 17: Option Storage Checksum 19: Module Voltage Mismatch 20: Unknown Module 21: Factory Configuration Error 22: Illegal Address 23: Series Mismatch 24: Open Slot | Major | CIP Motion
18 | 3 | Major Fault T18:C03 - CIP Motion Fault: A standard Axis Fault has been detected by the drive. | There is a fault on the physical axis. | To determine corrective action, see the Axis Fault attributes. The corresponding bit indicates the cause of the fault. | Major | CIP Motion
18 | 4 | Major Fault T18:C04 - CIP Motion Fault: A manufacturer specific Axis Fault has been detected by the drive. | There is a fault on the physical axis. This fault indicates a manufacturer-specific axis fault | To determine corrective action, see the Axis Fault Mfg attributes. The corresponding bit indicates the cause of the fault. | Major | CIP Motion
18 | 5 | Major Fault T18:C05 - CIP Motion Fault: A Motion Fault has been detected by the drive. | A CIP Motion fault detected. | To determine corrective action, see the Motion Fault attribute and Motion Fault bits for details about the fault that occurred. | Major | CIP Motion
18 | 6 | Major Fault T18:C06 - CIP Motion Fault: A Module Fault has been detected by the drive. | A CIP Motion drive fault detected. Usually the fault affects all the axes associated with the module and all of the associated axes are shut down. | Reconfigure the faulted motion module to correct the fault. | Major | CIP Motion
18 | 7 | Major Fault T18:C07 - CIP Motion Fault: Group Fault | A CIP Motion group fault detected. Usually the fault affects all of the axes associated with a motion group. | Reconfigure the entire motion subsystem to correct the fault. See the Group Fault attribute if details about the fault are needed. | Major | CIP Motion
18 | 8 | Major Fault T18:C08 - CIP Motion Fault: A Configuration Fault has been detected by the drive. | A fault occurred during the configuration of a CIP Motion drive. Typically, this fault occurs when an attempt to update an axis configuration attribute of a CIP Motion drive was unsuccessful. | To determine the corrective action, see the Configuration Fault in the Attribute Error Code and Attribute Error ID attributes associated with the motion or 1756-ENxT module. | Major | CIP Motion
18 | 9 | Major Fault T18:C09 - CIP Motion Fault: A standard APR Fault has been detected by the drive. | An Absolute Position Recovery (APR) fault occurred and the absolute position of the axis cannot be recovered. | To determine the corrective action, see the APR Fault attributes. The corresponding bit indicates the cause of the fault. 1: Memory Write Error 2: Memory Read Error 3: Feedback Serial Number Mismatch 4: Buffer Allocation Fault 5: Scaling Configuration Changed 6: Feedback Mode Changed 7: Feedback Integrity Loss | Major | CIP Motion
18 | 10 | Major Fault T18:C10 - CIP Motion Fault: A manufacturer specific APR Fault has been detected by the drive. | An Absolute Position Recovery (APR) Fault occurred and the absolute position of the axis cannot be recovered. This fault indicates a manufacturer-specific APR fault. | To determine the corrective action, see the APR Fault Mfg attributes. The corresponding bit indicates the cause of the fault. | Major | CIP Motion
18 | 128 | Major Fault T18:C128 - CIP Motion Fault: A Guard Fault has been detected by the drive. | A safety fault on the drive axis detected. | To determine the corrective action, see the GuardMotion™ attributes. The corresponding bit indicates the cause of the fault. | Major | CIP Motion
20 | 1 | Major Fault T20:C01 - License Fault: License is missing or invalid. | A required license is missing or expired during the transition to Run or Test mode. | Insert a CmCard containing all licenses required by the project in the controller. | Major | License Protection
20 | 2 | Minor Fault T20:C02 - License Fault: License has expired. | The License Based Execution Protection license stored on the CmCard has the correct license, but it has expired. | Obtain a CmCard with the correct unexpired license and insert it into the controller. | Minor | License Protection
21 | 1 | Minor Fault T21:C01 - Alarm Fault: Evaluating alarms exceeded the evaluation period. | Evaluating alarms exceeded the evaluation period. | If the fault occurs for a controller experiencing regular active alarm rate (i.e. not alarm burst) for Tag-based alarms during the system commissioning then reduce the number of the alarms in the project. Otherwise, the fault is an indicator for the operator to be aware that Tag-based alarm state information can be older than the evaluation period (only 500 ms evaluation period). | Minor | Alarm
21 | 2 | Minor Fault T21:C02 - Alarm Fault: Alarm set highest severity alarm data may be inaccurate. | Alarm set highest severity alarm data may be inaccurate. | If the fault occurs for a controller experiencing regular active alarm rate (i.e. not alarm burst) for Tag-based alarms during the system commissioning, then reduce the number of the alarms in the project. Otherwise, the fault is an indicator for the operator to be aware that information about the Alarm Set highest severity can be older than 2 seconds. | Minor | Alarm

## IO faults
Logix 5000™ Controller and I/O Fault Codes
These are controller-generated faults for I/O modules that the controller owns.
For more information, see:
http://literature.rockwellautomation.com/idc/groups/literature/documents/pm/1756-pm014_-en-p.pdf
Fault Type | Fault Code (I/O Map Object Attribute 5) | Studio 5000 Logix Designer® Application Display Text | Fault | Corrective Action
I/O | 0x0001 | Connection failure | A connection to a module failed. | Extended status codes in these ranges provide more detail as to the connection failure.
I/O | 0x0002 | Resource unavailable. | Possible causes include the following. • There are not enough connections available either for the controller or for the communication module being used to connect through. • The I/O memory limits of the controller are exceeded. • The I/O module that is targeted does not have enough connections available. | • Check the connection use of the controller or communication module. If all connections are used, try to free some of the used connections or add another module to route the errant connection through. • Check the I/O memory available and make program or tag changes if needed. • Check the number of controllers making a connection to this I/O module and verify that the number of connections is within the limits of the I/O module.
| 0x0003 | Invalid value in an object specific data parameter of a service request | A parameter that is associated with the request was invalid. | Possible causes include the following: The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options were used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
| 0x0004 | Connection Request Error: Bad Segment. | IOI segment error on connection request. | The target module does not like one of the parameters in the connection request. This may occur if improper module keying is being used or if the wrong map type attribute is set in the map entry.
| 0x0005 | Connection Request Error: Bad Class | The controller is attempting to make a connection to the module and has received an error. | Possible causes include the following: • The configured address for the connection to the module is incorrect. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options were used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of Logix Designer application. For more information about electronic keying, see the user manual for the module you are using. If you are using a 1756-DHRIO module, verify that the Channel type selected in the software (DH+™ or remote I/O network) matches the module’s rotary switch settings.
I/O | 0x0006 | Partial data transferred. | Only part of the expected data was transferred. | Possible causes include the following. • The response buffer is too small to handle the response data. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passed the electronic keying test. This may result when Disable Keying or Compatible Keying options were used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0x0007 | Messaging connection lost. | The messaging connection was lost. | A service request is unconnected, but should be connected.
I/O | 0x0008 | Service Request Error: Unsupported Service | The controller is attempting to request a service from the module that is not supported by the module. | Possible causes include the following. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passed the electronic keying test. This may result when Disable Keying or Compatible Keying options were used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0x0009 | Module Configuration Rejected: parameter error. | The configuration for the module is invalid. The module configuration may have been changed in the Data Monitor or programmatically. | • Additional Fault Information for this fault will be displayed as a hex code on the Connection Tab. If available for the module, open the Connections tab of the Module Properties dialog box for the additional fault code. The additional fault code indicates the configuration parameter that is causing the fault. You may have to correct multiple parameters before this fault is cleared and the module is connected. •Verify that the configuration is valid by using the module configuration software to validate your configuration. Consult the module documentation for a list of fault codes to determine the configuration parameter that is in error.
I/O | 0x000A | An attribute in the Get_Attributes_List or Set_Attributes_List has a non-zero status. | Possible causes include the following. • A connection is being created where the connection type is invalid. • An object attribute or tag value is invalid. | If an object attribute or tag is invalid, export the Logix Designer application file, then re-import it. Reschedule the ControlNet® network after re-importing if applicable.
I/O | 0x000B | Object already in requested mode or state | The object is already in the mode/state being requested by the service. | You do not have to request a mode/state because the object is already in the requested mode/state.
I/O | 0x000C | Service Request Error: Invalid mode or state for service request. | The controller is attempting to request a service from the module and has received an error. | First, verify that the module is not faulted. For an I/O module, this may indicate that the module has one of the following conditions: • Limited communication is possible, but the module has a Major Fault. • A firmware update needs to be completed or is currently being completed. Refer to the Module Info tab to determine the exact cause.
I/O | 0x000D | Object Already Exists | An object instance is created where the instance already exists. | Use a different object instance number.
I/O | 0x000E | Attribute value not settable. | A MSG instruction is configured to change an attribute that cannot be changed. | See the device user manual for available programming options.
I/O | 0x000F | Access permission denied for requested service. | A MSG instruction has been configured to delete a map object that cannot be deleted. | See the device user manual for available programming options.
I/O | 0x0010 | Mode or state of module does not allow object to perform requested service. | The state of the device prevents a service request from being handled. | See the device user manual for available programming options.
I/O | 0x0011 | Reply data too large. | The reply to a message has a data size that is too large for the destination. | Change the destination to a tag that can handle the data size and type being returned.
I/O | 0x0012 | Requested service specifies an operation that is going to fragment a primitive data value. | The service specified an operation that is going to fragment a primitive data value, i.e. half a REAL data type. | The size of the data being read or written must be rounded to the next primitive data type size. The service is operating on data that is too large for the underlying communication size limits.
I/O | 0x0013 | Module Configuration Rejected: Data size too small. | The configuration for the module is invalid. Not enough configuration data was sent. | Verify that the correct module is being targeted.
I/O | 0x0014 | Undefined or unsupported attribute. | A MSG instruction is configured to change an attribute that does not exist. | See the device user manual for available programming options.
I/O | 0x0015 | Module Configuration Rejected: Data size too large. | The configuration for the module is invalid. Too much configuration data was sent. | Verify that the correct module is being targeted.
I/O | 0x0100 | Connection Request Error: Module in Use. | The connection being accessed is already in use. | Check for these conditions: • The controller is attempting to make a specific connection to a module and the module cannot support more than one of these connections. • The target of a connection recognizes that the owner is attempting to remake a connection that is already running.
I/O | 0x0103 | Service Request Error: CIP™ transport class not supported. | This indicates that the controller is requesting a transport class that is not supported by the module. | Check for these conditions: • The controller is requesting services not supported by the module. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passed the electronic keying test. This may result when Disable Keying or Compatible Keying options were used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0x0106 | Connection Request Error: Module owned and configured by another controller. Module may accept only one connection if Unicast is used. | An ownership conflict occurred for the connection. | Check for these conditions: • The Connection Request to this module has been rejected due to an Ownership conflict with another Owner (for example, another Controller). This may occur with modules, such as output modules, that allow only one Owner to configure and control its outputs. This fault may also occur if the module is configured as Listen Only and supports only one connection. • If the Owner is connected to the module with a Unicast connection over EtherNet/IP™ network, other connections to the module may fail because the Owner controls the one connection. • If the Owner is connected to the module with a Multicast connection over EtherNet/IP network, Unicast connections to the module may fail because the Owner controls the one connection. Configure both the Owner and the Listen Only connection as Multicast.
I/O | 0x0107 | Connection Request Error: Target Connection Not Found. | A connection being accessed was not found. | Check for these conditions: • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. • The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options are used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using. • You have configured a consumed tag or module to use a Unicast connection over EtherNet/IP network, but the producer does not support Unicast connections.
I/O | 0x0108 | Connection Request Error: Connection type (Multicast/Unicast) not supported. | The controller is requesting a connection type that is not supported by the module. | Check for these conditions: • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. • The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options are used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using. • You have configured a consumed tag or module to use a Unicast connection over EtherNet/IP network, but the producer does not support Unicast connections.
I/O | 0x0109 | Connection Request Error: Invalid connection size. | The connection size is inconsistent with the expected size. | Additional Error Information for this fault will be displayed as the tag name associated with the connection instance number that has the fault. Check for these conditions: • The controller is attempting to set up a connection with the module and cannot because the size of the connection is invalid. • The controller may be attempting to connect to a tag in a producing controller whose size does not match the tag in this controller. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. • The fault may occur even when the module passed the electronic keying test. This may result when Disable Keying or Compatible Keying options were used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using. If the module is a 1756 ControlNet module, verify that the chassis size is correct. For remote I/O adapters, verify that the rack size and rack density is correct.
I/O | 0x0110 | Connection Request Error: Module not configured. | The controller is attempting to set up a Listen Only connection with the module and cannot because the module has not been configured and connected to by an Owner (for example, another controller). | This controller is not an Owner of this module because it is attempting to establish a Listen Only connection, which requires no module configuration. The controller cannot connect until an Owner configures and connects to the module first.
I/O | 0x0111 | Requested Packet Interval (RPI) out of range. | RPI not supported. | Check for these conditions: • The Requested Packet Interval (RPI) specified is invalid for this module or for a module in the path to this module. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options are used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using. • For Listen Only connections: the RPI set by the owner of this module is slower than the one requested. Either increase the requested RPI or decrease the RPI the owner controller is using. See the Connection tab for valid RPI values.
I/O | 0x0113 | Connection Request Error: Module connection limit exceeded. | The number of connections is greater than what is available on the module. The number of connections must be reduced or the hardware must be upgraded. | To reduce the number of connections: • Change the FLEX™ I/O communication adapter Comm Format from Input or Output configuration to Rack Optimization. When the Comm Format changes, the adapter must be removed and recreated in the I/O configuration tree. • If the configuration uses messaging over ControlNet, sequence the messages to reduce the number that are executing at the same time, or reduce the number of messages. Messages (MSG instructions) also use connections.
I/O | 0x0114 | Electronic Keying Mismatch: Electronic keying product code and/or vendor ID mismatch. | The Product Code of the actual module hardware does not match the Product Code of the module created in the software. | Electronic Keying failed for this module. You may have a mismatch between the module that is created in the software and the actual module hardware.
I/O | 0x0115 | Electronic Keying Mismatch: Electronic Keying product type mismatch. | The Product Type of the actual module hardware does not match the Product Type of the module created in the software. | Electronic Keying failed for this module. You may have a mismatch between the module created in the software and the actual module hardware.
I/O | 0x0116 | Electronic Keying Mismatch: Major and/or Minor revision invalid or incorrect. | The Major or Minor revisions of the module do not match the Major or Minor revisions of the module created in the software. | Electronic Keying failed for this module. • Verify that you have specified the correct Major and Minor Revision if you have chosen Compatible Module or Exact Match keying. • You may have a mismatch between the module created in the software and the actual module hardware.
I/O | 0x0117 | Connection Request Error: Invalid Connection Point. | The connection is to an invalid port or port that is already in use. | Additional Error Information for this fault appears as the tag name associated with the controller to controller (C2C) that has the fault. Check for these conditions: • Another controller owns this module and has connected with a Communications Format different than the one chosen by this controller. Verify that the Communications Format chosen is identical to that chosen by the first owner controller of the module. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passed the electronic keying test. This may result when Disable Keying or Compatible Keying options were used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using. • The controller may be attempting to connect to a nonexistent tag in a producing controller.
I/O | 0x0118 | Module Configuration Rejected: Format error. | An invalid configuration format was used. | Check for these conditions: • The configuration class specified does not match the class supported by the module. • The connection instance is not recognized by the module. • The path specified for the connection is inconsistent. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passed the electronic keying test. This may result when Disable Keying or Compatible Keying options were used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0x0119 | Connection Request Error: Module not owned. | The controlling connection is not open. | Where a Listen Only connection is requested, the controlling connection is not open.
I/O | 0x011A | Connection Request Error: Out of Connection Resources | The controller is attempting to set up a connection with the module and cannot because required resources are unavailable. | • If the module is a 1756 ControlNet module, up to five controllers can make Rack Optimization connections to the module. Verify that this number has not been exceeded. • If the module is a 1794-ACN15, 1794-ACNR15, or 1797-ACNR15 adapter, only one controller can make a Rack Optimization connection to the module. Verify that this number has not been exceeded.
I/O | 0x0203 | Connection timed out. | The owner or originator recognizes that the target device is on the network or backplane. However, I/O data and messages are not being responded to. | The target can be reached, but its response is not as expected. For example, this fault may be indicated where multicast Ethernet packets are not returned. When this fault occurs, the controller usually attempts to continuously remove and remake the connection. If you use FLEX I/O modules, verify that you are using the correct terminal device.
I/O | 0x0204 | Connection Request Error: Connection request timed out. | The controller is attempting to make a connection; however, the target module is not responding. The device also appears to be missing from the backplane or network. | To recover, take the following steps. • Verify that the module has not been removed and is still functioning and receiving power. • Verify that the correct slot number has been specified. • Verify that the module is properly connected to the network. If you are using FLEX I/O modules, verify that the correct terminal block is in use.
I/O | 0x0205 | Connection Request Error: Invalid parameter. | The controller is attempting to set up a connection with the module and has received an error (a parameter is in error). | The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options are used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0x0206 | Connection Request Error: Requested size too large. | The controller is attempting to set up a connection with the module and has received an error - the request size is too large. | Either: • Verify that the path to this module is sufficiently close to the controller. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options are used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0x0301 | Connection Request Error: Out of buffer memory. | The controller is attempting to set up a connection with the module and has received an error: a module in the path is out of memory. | Check for these conditions: • The controller may be attempting to connect to a tag in a producing controller that is not marked as being produced. • The controller may be attempting to connect to a tag in a producing controller. That tag may not be configured to allow enough consumers. • The size or number of connections through this module needs to be reduced. • One of the network modules between the module and the controller may be out of memory. Check network configuration of the system. • The module may be out of memory. Check the system configuration and capabilities of the module. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options are used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0x0302 | Connection Request Error: Out of communication bandwidth. | The controller is attempting to set up a connection with the module and has received an error: a module in the path has exceeded its communication bandwidth capacity. | Increase the Requested Packet Interval (RPI) and reconfigure your network with RSNetWorx™ software. Distribute the load on another bridge module.
I/O | 0x0303 | Connection Request Error: No bridge available. | The controller is attempting to set up a connection with the module and has received an error: a module in the path has exceeded its communication bandwidth capacity. | Distribute the load on another bridge module.
I/O | 0x0304 | Not configured to send scheduled data. | The ControlNet module is not scheduled to send data. | Use RSNetWorx for ControlNet software to schedule or reschedule the ControlNet network.
I/O | 0x0305 | Connection Request Error: ControlNet configuration in controller does not match configuration in bridge. | The ControlNet configuration in the controller does not match the configuration in the bridge module. This may occur because a ControlNet module was changed after the network was scheduled, or because a new control program has been loaded into the controller. | Use RSNetWorx for ControlNet software to reschedule the connections.
I/O | 0x0306 | ControlNet Keeper not available.. | The ControlNet Configuration Master (CCM) cannot be found. The 1756-CNB module and PLC-5® ControlNet processor are the only devices capable of being a CCM and the CCM must be node 1. This fault may temporarily occur when the system is powered up and is being cleared when the CCM is located. | Verify that a 1756-CNB modules or PLC-5 ControlNet processor is at node 1 and is functioning properly.
I/O | 0x0311 | Connection Request Error: Invalid port. | The controller is attempting to set up a connection with the module and has received an error. | Verify that all modules in the I/O Configuration tree are the correct modules.
I/O | 0x0312 | Connection Request Error: Invalid link address. | The controller is attempting to set up a connection with the module and has received an error: an invalid link address has been specified. A link address can be a slot number, a network address, or the remote I/O chassis number and starting group. | • Verify that the chosen slot number for this module is not greater than the size of the rack. • Verify that the ControlNet node number is not greater than the maximum node number configured for the network in RSNetWorx for ControlNet software.
I/O | 0x0315 | Connection Request Error: Invalid segment type. | The segment type or route is invalid. | Either: • The controller is attempting to set up a connection with the module and has received an error: the connection request is invalid. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options are used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0x0317 | Connection Request Error: Connection not scheduled. | The controller is attempting to set up a ControlNet connection with the module and has received an error. | Use RSNetWorx for ControlNet software to schedule or reschedule the connection to this module.
I/O | 0x0318 | Connection Request Error: Invalid link address - cannot route to self. | The controller is attempting to set up a connection with the module and has received an error: the link address is invalid. | Verify that the associated ControlNet module has the correct slot or node number selected.
I/O | 0x0319 | Connection Request Error: No secondary resources available in redundant chassis. | The controller is attempting to set up a connection with the module and has received an error: the redundant module does not have the necessary resources to support the connection. | Reduce the size or number of connections through this module or add another controller or ControlNet module to the system.
I/O | 0x031B | Connection Request Error: Rack Connection Refused. | The controller is attempting to set up a Direct connection with the module and has received an error. | A rack-optimized connection has already been established to this module through the 1756-CNB/R in the same chassis. • Connect to this module via the 1756-CNB/R in the same chassis. • Connect to this module via a different 1756-CNB/R to use a Direct connection. • Change the first connection from rack-optimized to Direct, and then re-establish the second direct connection. • Connect to this module from a controller in the same chassis as the module (do not connect via 1756-CNB/R.
I/O | 0x031E | Connection Request Error: Cannot consume tag. | The controller is attempting to connect to a tag in a producing controller and has received an error. | • The controller is attempting to connect to a tag in a producing controller and that tag has already been used by too many consumers. • Increase the maximum number of consumers on the tag.
| 0x031F | Connection Request Error: Tag not published. | The Consume tag was not configured to be produced in the target module. | Make sure the name of the tag being consumed is spelled correctly in both the consumer and producer.
I/O | 0x0322 | Connection Request Error: Data format for requested connection does not match data format of connection already established. | A new connection requested does not match the existing connection. | Check the controllers that are using the connection and verify that all configurations are identical.
I/O | 0x0800 | Network link in path to module is offline. | A bridge module in the path to the target module is offline. | It is either not physically connected to the network (media disconnected) or otherwise unable to forward the request onto the destination network.
I/O | 0x0801 | Incompatible Multicast RPI | A connection has already been established to the target module at a different RPI and it cannot be changed to accommodate the RPI specified. | • Configure the tag as unicast. • Adjust RPI so that all multicast consumers of the tag use the same RPI. • Configure the RPI so that is in the range allowed by the producer.
I/O | 0x0810 | No target application data available. | The controlling application has not initialized the data to be produced by the target device. This may be caused when "Send Data" connections are configured in a target device and the controlling application for that target device has not initialized the data to be produced. | For the target device associated with the "Send Data" connection reporting this connection error, start the controlling application and perform at least one write of data. See the documentation for the target device and its controlling application for information on how to do this.
I/O | 0x0814 | Connection Request Error: Data Type Mismatch. | Given data type does not match Produce tag data type in target module. | Make sure both data types match.
I/O | 0xFD01 | Connection Request Error: Bad Backplane EEPROM. | Bad Backplane EEPROM. | Replace the backplane.
I/O | 0xFD02 | Connection Request Error: No error code is supplied by an I/O module to describe an I/O fault. | No error code is supplied by an I/O module to describe an I/O fault. | See the user manual for your device.
I/O | 0xFD03 | Connection Request Error: Required Connection missing | The controller is attempting to set up a connection with the module and has received an error. | This module requires a particular set of connections and connection types, and one of those connection types is missing.
I/O | 0xFD04 | Connection Request Error: No CST Master Detected | The controller is attempting to set up a connection with the module and has received an error - this module requires a CST master in the chassis. | Configure a module (typically a controller) in this chassis to be the CST master.
I/O | 0xFD05 | Connection Request Error: No Axis or Group Assigned. | The controller is attempting to set up a connection with the module and has received an error - this module requires an axis or group table assigned. | Assign a Group or Axis.
I/O | 0xFD06 | SERCOS Transition Fault | The controller command to transition the SERCOS ring to a new phase returned an error from the module. | Check for duplicate Drive Nodes.
I/O | 0xFD07 | Connection Request Error: SERCOS Init Ring Fault. | An attempt to configure the SERCOS ring failed. | The baud rate for all devices must be the same and supported by the drives and the SERCOS module.
I/O | 0xFD08 | SERCOS Comm Fault | Mainly two sets of faults may cause this fault, physical and interface faults. Interface errors are encountered when you are configuring third-party drives. | Check for these sources of physical faults: • Broken ring • Loose connector • Fiber optics not clean • Electrical noise due to improper drive grounding • Too many nodes on the ring Check for these potential interface errors: • No SERCOS MST (Protocol Error). • Missed AT (drive did not send data when expected). • SERCOS timing error in phase 3. • Error in drive data that is returned to SERCOS module.
I/O | 0xFD09 | SERCOS Node Initialization Fault | The SERCOS module defected a problem during the Init Node Comm service. | There is a problem with the IDNs being configured. Check the general and extended error codes and refer to their definition SERCOS documentation.
I/O | 0xFD0A | Axis Attribute Error - See Faulted Axis. | The Analog Servo Motion Module Rejected an attribute update. | Ensure all attributes are set to valid values. See Analog axis attribute documentation.
I/O | 0xFD0C | The end device has a different Grandmaster than the controller | The CIP Motion Drive detected a different PTP Grandmaster than the controller. | Ensure the CIP Motion drive and the controller can synchronize to the same CIP Sync™ grandmaster clock. See the Time Synchronization page for the drive and the controller.
I/O | 0xFD1F | Bad Safety Protocol Format. | An error occurred adding the safety network segment to a route. | • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options are used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0xFD20 | No safety task running in local controller. | No safety task appears to be running. | Safety modules require that a safety task be present and running in the controller originating the connection.
I/O | 0xFD22 | POINTBus™ Fault: The configured number of expansion I/O modules does not match the number of physical modules detected. | When the expected chassis size does not match the discovered chassis size, I/O connections are prevented. | Verify the number of physical expansion I/O modules configured for the controller and then update the number of modules selected from the Expansion I/O list on the General page in the Controller Properties dialog.
I/O | 0xFD23 | PointBus Fault: Expansion modules detected beyond the number allowed for this controller type. | This error can happen when you put more modules in a chassis than what the product catalog supports. You cannot detect the extra modules using a tool like RSLinx® as that only lets you browse up to the chassis size. When you try to establish I/O connections, I/O connections are prevented. | To verify the number of physical expansion I/O the controller supports, open the Controller Properties dialog and expand the Expansion I/O list on the General page. Configure the number of physical expansion I/O modules to match the selection in the Expansion I/O list.
I/O | 0xFE01 | Connection Request Error: An invalid configuration format was encountered. | An invalid configuration format was encountered. | The connection type configured by the profile is not appropriate for this module.
I/O | 0xFE02 | Requested Packet Interval (RPI) out of range. | The Requested Packet Interval (RPI) specified is invalid for this module. | See the Connection tab for valid RPI values.
I/O | 0xFE03 | Connection Request Error: The input connection point has not been set. | Invalid input connection point. | The input connection point is 0 and is not allowed to be 0.
I/O | 0xFE04 | Connection Request Error: Invalid input data pointer. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE05 | Connection Request Error: Invalid input data size. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE06 | Connection Request Error: The input force pointer has not been set. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE07 | Connection Request Error: The output connection point has not been set. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE08 | Connection Request Error: Invalid output data pointer. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE09 | Connection Request Error: Invalid output data size. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE0A | Connection Request Error: The output force pointer has not been set. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE0B | Invalid Symbol String | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE0C | Invalid PLC-5 instance number. | The controller is attempting to set up a connection with the PLC-5 controller and has received an error. | Verify that the instance number specified has been properly specified in the PLC-5 controller.
I/O | 0xFE0D | Tag does not exist in peer controller. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE0E | Automatic Firmware Update in progress. | The module is currently being updated. | This is not an error, but an information code
I/O | 0xFE0F | Automatic Firmware Update Failed: Firmware file incompatible with the module. | Firmware Supervisor has attempted to update an unsupported module. This occurs when there is no NVS file on the SD card for the module revision specified in the project. | Either: • Update Module firmware file on SD card with proper module revision. • Change module revision in the module properties in the project.
I/O | 0xFE10 | Automatic Firmware Update Failed: Firmware file not found. | The firmware file to update the module cannot be found. The project has a module that needs a specific firmware revision that is not on the SD card. | Either: • Manually update the module's firmware. • Copy the correct revision of module firmware to the SD card. • Change the module revision in the project to match the revision on the module.
I/O | 0xFE11 | Automatic Firmware Update Failed: Firmware file invalid. | The firmware file is corrupted. | Either: • Use a different SD card. • Copy the correct revision of module firmware to the SD card.
I/O | 0xFE12 | Automatic Firmware Update Failed. | An error has occurred while updating the module. | Check the module status indicators, and troubleshoot the module.
I/O | 0xFE13 | Automatic Firmware Update Failed: Detected Active Connections. | An active connection could not be made to the target module. | There is an active connection already made to the target module from some other originator, thereby disallowing a flash update from occurring.
I/O | 0xFE14 | Automatic Firmware Update pending: Searching NVS file for appropriate module identity. | The firmware file is currently being read. | Firmware Supervisor is searching NVS File for identity info. This is not an error, but an information code.
I/O | 0xFE22 | Connection Request Error: Invalid input network connection type. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFE23 | Connection Request Error: input connection does not specify whether unicast is allowed. | Module entry in the controller incorrect. | Contact Rockwell Automation Support.
I/O | 0xFF00 | Connection Request Error: No connection instance. | The controller is attempting to set up a connection with the module and has received an error. | • Verify that the physical module is the same module type (or is a compatible module) as created in the software. • If the module is a 1756-DHRIO module in a remote chassis (connected via a ControlNet network), verify that the network has been scheduled with RSNetWorx software. • Even after the network has been scheduled with RSNetWorx for ControlNet software, if you are online and if the 1756-DHRIO module is configured for DH+ network only, a 0xff00 Module Fault (no connection instance) may occur. The module is properly communicating even though Faulted is displayed as its Status on the Module Properties dialog box. Disregard the error message and fault status and continue.
I/O | 0xFF01 | Connection Request Error: Path to module too long. | The controller is attempting to set up a connection with the module and has received an error. | Verify that the path to this module is a valid length.
I/O | 0xFF04 | Connection Request Error: The controller's map instance attempted to access a connection while being in an invalid state. | The remote controller’s map instance attempted to access a connection while in an invalid state. An attempt was made to initiate the reconfiguration of a device that is not supported by the controller | Go offline with the controller and make the change and then download the modified project to the controller.
I/O | 0xFF08 | Connection Request Error: Invalid path to module. | The controller is attempting to set up a connection with the module and has received an error. | Verify that the path to this module is a valid length.
I/O | 0xFF0B | Module Configuration Rejected: Bad format. | Invalid configuration format. | Either: • The configuration for the module is invalid. • The module in use (that is, the physical module) is different than the module specified in the I/O configuration tree and is therefore causing the connection or service to fail. The fault may occur even when the module passes the electronic keying test. This may result when Disable Keying or Compatible Keying options are used in the module configuration instead of the Exact Match option. Despite passing the electronic keying test, the module being connected to does not have the same features or settings as the module specified in the I/O configuration tree and does not support the connection or service being attempted. Check the module in use and verify that it exactly matches the module specified in the I/O configuration tree of the Logix Designer application. For more information about electronic keying, see the user manual for the module you are using.
I/O | 0xFF0E | Connection Request Error: No connections accepted to bridge. | The controller is attempting to set up a connection with a ControlNet bridge module and has received an error. | ControlNet bridge modules should not have connections to them.